Specification Writer…select appropriate option for all items shown in RED.

This specification is a master document that must be edited for each project specific scope.  This design is intended for systems with a potential two addressable fire loops for a complete Commercial Fire Alarm System with all components.

- FIRE ALARM SYSTEM SPECIFICATION

- GENERAL

- RELATED DOCUMENTS:

  - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

- SYSTEM CAPACITY SUMMARY:

  - Napco C Series Gemini Fire-Alarm addressable control with capacity up to 255 devices including wireless. Per NFPA 72 UL864 9th Ed., UL 985 approved.

  - Support up to 32 AH battery backup @ 24VDC

  - Addressable Smoke detectors with auto-drift compensation & maintenance alert

  - Addressable Heat detectors

  - Addressable Duct smoke detectors

  - Manual addressable fire-alarm pull stations

  - Addressable modules for conventional & legacy devices

  - Addressable SLC Loop Isolator optional for required applications

  - Built in Synch/Strobe/Horn module on each NAC for Notification appliances

  - Supports up to (255) Wireless Fire Devices for addressability of all devices

  - Supports up to (4) on-board NAC power supplies 6.5A capacity, expand to (24)

  - Supports from one to seven GEMC-FK1 Fire Keypads anywhere on the buss

  - Support Conventional Zone modules

  - Support Conventional Zone Expander

  - Support up to (96) Outputs

  - Onboard Digital Alarm Communicator Transmitter, Dual Line

  - Optional TCP/IP reporting

  - Support System Printer

- BASE SYSTEM DESCRIPTION:

  - Napco Commercial Gem-C Firewolf Fire System, UL Listed intelligent addressable fire alarm system with multiplexed signal transmission.  The System supplied under this specification shall utilize independently addressed, input/output modules and power supply(s) as described in this specification.  This system has been specified using the NAPCO Gem-C Firewolf Series Fire Alarm control panel and related devices with NAC power supply(s), with supported devices listed.  All references to manufacturer's model numbers and other pertinent information herein is intended to establish minimum standards of performance, functionality and quality.  Equivalent compatible UL-listed equipment may be substituted from other manufacturers for the specified equipment as long as these minimum standards are met and the submittals are approved for the content, operation and viability of the system.

- SUBMITTALS:

  - The Contractor shall purchase no equipment for the system specified herein until the Owner has approved the project submittal in its entirety and has returned their comments to the contractor.  It is the responsibility of the contractor to meet the entire intent and functional performance detailed in these specifications for the design and future expansion.  Approved submittals shall only allow the contractor to proceed with the installation and shall not be construed to mean that the contractor has satisfied the requirements of these specifications.  The Contractor shall submit three (3) complete sets of documentation within 30 calendar days after award of the purchase order.

  - Submittals and drawings shall also be approved by authorities having jurisdiction simultaneously or prior to submitting them to the Architect.  Shop Drawings shall be prepared by persons with the following qualifications:

    - Trained and document certified by manufacturer in fire-alarm system design.

    - NICET-certified fire-alarm technician, Level II minimum

    - Product Data:  Product Data sheets with the printed logo or trademark of only one manufacturer of all the equipment.  Indicated in the documentation shall be the type, size, rating, style, and catalog number for all items proposed to meet the system performance detailed in this specification.  The proposed equipment shall be subject to the approval of the Owner's representative and AHJ.

    - Shop Drawings:  Include plans, elevations, sections, details and attachments to other work.

    - All references to manufacturer's model numbers and other pertinent information herein is intended to establish minimum standards.  See F. 1. above.

- MANUALS:

  - Submit (3) sets of complete operating and maintenance manuals listing the manufacturer's name(s), including technical data sheets with approved "as built" drawings at the completion of the final test for approvals.  Include a Sequence of Operation.  The project is not complete until the O & M manuals are submitted and found acceptable.

  - Wiring diagrams shall indicate internal wiring for each device and the interconnections between the items of equipment with all wire runs, conductors & length of wire.

  - Provide a clear and concise description of operation that gives in detail, the information required to properly operate the equipment and system.

- SOFTWARE MODIFICATIONS:

  - Provide the services of a factory trained and qualified technician to perform all system software modifications, upgrades or changes during the one year warranty period.  Response time of the technician to the site shall not exceed 4 hours.

  - Comply with recommendations in the "Documentation" Section of the "Fundamentals of Fire Alarm Systems" Chapter in NFPA72.  Include voltage drop calculations for notification appliance circuits.  Include battery-size calculations.

  - Include performance parameters and installation details for each listed detector, verifying each is listed for complete range of air velocity, temperature, and humidity possible when air-handling systems are operating.  Include plans, sections, and elevations drawn to scale and coordinating installation of duct smoke detectors and access to them.  Show critical dimensions that relate to placement and support of sampling tubes, detector housing, and remote status and alarm indicators.  Locate detectors according to manufacturer's written recommendations in straight runs of duct.

- OPERATION & MAINTENANCE DATA:

  - List all fire alarm devices and components to be included in operation, and maintenance manuals as described in G. 1.

  - Comply with the "Records" Section of the "Inspection, Testing and Maintenance" Chapter in NFPA72.  Provide "Record of Completion Documents" according to NFPA72 article "Permanent Records" in the "Records" Section of the "Inspection, Testing and Maintenance" Chapter.  Provide "Maintenance, Inspection and Testing Records" according to NFPA72 article of the same name and include:

    - Frequency of testing of installed components.

    - Frequency of inspection of installed components.

    - Requirements and recommendations related to results of maintenance.

    - Manufacturer's User Training manuals (3-hardcopy and 1-electronic on CD).

    - Manufacturer's required maintenance with system warranty requirements.

    - Program Software Data backup on (1) magnetic media or compact disk.

    - Device address list accompanying "as built" drawings.

    - Provide a list of system settings with a list of the contents of each panel.

    - Printout a Smoke Obscuration Report of all smoke detectors and their status.

    - Proprietary system/service companies will not be acceptable.

- PRODUCTS

  - FIRE-ALARM CONTROL UNIT

    - The control panel shall be Napco C Series Gemini Fire-Alarm addressable control with capacity up to 255 devices hardwired or wireless.  The system shall be designed specifically to provide (1) (2) Addressable SLC Loop Controller(s) for fire detection application.  The control panel shall include all required hardware, software and system programming to provide a complete and operational system designed to support herein, select as needed to match panel;

      - GEMC-FW-32KT 32 point GEM-C fire kit commercial control*

      - GEMC-FW-32CNVKT 32 point GEM-C fire kit commercial conventional control*

      - GEMC-FW-128KT 128 point GEM-C fire kit commercial control**

      - GEMC-FW-255KT 255 point GEM-C fire kit commercial control**

      - * Enclosure for use with 32KT above (16" X 14.25" X 5.2") one SLC, steel painted red.  Fits between enclosure studs on 16" centers.  NEMA-1.

      - ** Enclosure for use with 128KT or 255KT, as above (24" X 14.25" X 5.2")

      - 4 ampere GEMA-PSV4A-R or 7 ampere GEMA-PSV7A-R power supply

      - (1) or (2) GEMC-FW-SLC Fire Loop Module(s)

      - (  ) quantity of GEMC-FK1 LCD Fire Red Fire Keypad(s) (maximum of seven)

      - GEMC-F8ZCPIM Conventional 8-zone, 2-wire fire input module (one)

      - (1-4 ) GEMC-EZM8 8-point expansion module (0 to 4 Max on fire buss)

      - (1) GEMC-NL- MOD Internet reporting module (one)

      - (  ) FWC-FSLC-SMK Addressable-Analog photo-electric smoke detector(s). (check device count)***

      - (  ) FWC-FSLC-HEAT Addressable-Analog heat detector(s), adjustable temp range (check device count)***

      - (  ) FWC-FSLC-SMK6B 6" base for smoke & heat detector(s) (not an addressable device.  See above smoke & heat detectors)

      - (  ) FWC-FSLC-DUCT Addressable-Analog photo-electric Duct smoke detector(s) with integral base-enclosure. (check device count)***

      - (  ) FWC-FSLC-EZM1 Addressable SLC 1-zone conventional expansion module (s), (counts as only one address on SLC loop, Max of 1) (check device count)*** (or see #17 below)

      - (  ) FWC-FSLC-EZM2 Addressable SLC 2-zone conventional expansion module (s), (counts as only one address on SLC loop. Max of 1) (only one of either EZM1 or EZM2)***

      - (  ) FWC-FSLC-CZM Addressable SLC single module(s) for Dry Contact Device (check device count)***

      - (  ) FWC-FSLC-RM2 Addressable SLC 2-output module(s), (counts as only one address on SLC loop. (Check device count)***

      - (  ) FWC-FSLC-ISO Addressable SLC short circuit module(s), special for Class A, Style 7 applications (check device count)***

      - (  ) FWC-FSLC-SOM1 Addressable SLC fire supervised output module(s), Used for elevator recall, HVAC shutdown, or added NAC w/ power supply. (check device count)***

      - (  ) FWC-FSLC-PULL Addressable SLC Fire Pull Station(s) (check device count)***

      - (1-4) GEMC-REVC Gemini Commercial Wireless (255) point RF receiver expansion module (Allowed up to 4 per system maximum.)

      - (  ) GEMC-WL-SMK Wireless Addressable photo-electric smoke detector(s) (check device count)***

      - (  ) GEMC-WL-HEAT Wireless Addressable heat detector(s) 135 deg. (check device count)***

      - (  ) GEMC-WL-WD2 Wireless Addressable 2-input module (s) to supervise Flows, tampers, legacy devices, etc. (check device count)***

      - (  ) FWC-FSLC-PROG2 Tool for Address-Program of SLC devices

      - GEMC-NAC7 Remote 4-output NAC extender on any one output.  (See red enclosure above * required for this use)

      - GEMC-12V2APS-CF 12VDC power supply for fire buss, remote supervised.  Supports (2) each, uses 7AH 12 volt batteries.

      - GEMC-FPRINT parallel printer module.  (If printer desired)

      - GEMC-RM3008 8-form 'C' relay output module.

      - GEMC-RS232 RS232 adapter for serial output from panel.

      - GEMC-OUT8 PGM output module for 8-open collector PGM outputs.

      - ***NOTE:  Verify all addressable devices for final count to avoid exceeding the total supported by the panel selected.

- SYSTEM PRINTER

Utilize optional on site dot matrix, parallel printer with GEMC-FPRINT printer module.  This will provide a printout of the following events:  On receipt of signal, print alarm, supervisory, and trouble events.  Identify zone, device, and function.  Include type of signal (alarm, supervisory, or trouble) and date and time of occurrence.  Differentiate alarm signals from all other printed indications.  Print system reset events, including the information for device, location, date, time and a historical log of events.  One control panel shall be capable of supporting one printer.

- NOTIFICATION APPLIANCES

  - All Audio Visual appliances shall be of the same manufacturer as the Fire Alarm Control Panel or as recommended by the manufacturer to insure compatibility between the appliances and the control panel.  Verify that the installations of the A/V appliances are completed in accordance with the manufacturers' instructions.  Candela requirements are to be met in all locations.  Any appliances, which do not meet the above requirements, and are submitted, for use must show written proof of they are compatible for the purpose intended.  All appliances shall be UL listed Fire Protective Service for use with this panel.

  - Visual Devices:  Provide wall or ceiling mounted base (red or white) with clear strobes and screw terminals.  Strobes shall provide a smooth light distribution pattern field selectable candela 15 cd, 30 cd, 75 cd, and 110 cd flash output rating.  Ceiling mounted devices shall have selectable candela settings of 15cd, 30cd, 75cd and 95cd, or 95cd, 115cd, 150cd, and 177cd.  All strobes shall be synchronized by the internal NAC or remote power supplies.

  - Audible Devices:  Provide low profile wall mounted A/V horns at the locations shown on the drawings.  The horn shall provide approx. 95 dBA sound output at 10 ft. when measured in reverberation room per UL-464.  The horn shall have a selectable steady or synchronized temporal output.  The horn shall mount in a 1-gang electrical box.

  - Audible/Visual Device:  Provide low profile wall mount horn/strobes at the locations shown on the drawings.  The horn/strobe shall provide an audible output of approx. 95 dBA at 10 feet when measured in reverberation room per UL-464.  Strobes shall provide synchronized flash outputs as described above.  Separate screw terminals shall be provided for wiring for each device.  Low profile horn/strobes shall mount to one-gang electrical box.

- MAGNETIC DOOR HOLDERS

Description:  Units are designed for wall or floor mounting as indicated and are complete with matching doorplate.  Mount as manufacturer recommends for a durable installation.  Electromagnet requires no more than 3 W to develop 25-lbf holding force.  Wall-Mounted Units shall fit flush mounted unless otherwise indicated.  Rating:  120-V ac, 24-V ac or dc.

- EXECUTION

  - Comply with NFPA 72 and NEC requirements for all installed devices.  Identify system components, wiring, cabling and terminals.  Comply with requirements for identification specified in Division 16 Section Electrical.  Install framed instructions in a location visible from fire-alarm control unit acceptable to the AHJ.

  - Equipment Mounting: Install fire-alarm control unit at 72" AFF with tops of cabinets not more than 72 inches above the finished floor.

  - New components shall be capable of merging with existing system configuration without degrading the performance of either system.  Existing system must be made compatible with any new devices by interface.

  - Smoke and Heat Detector Spacing:  Smooth ceiling spacing shall not exceed 30 feet or as required in NFPA 72.  Spacing of detectors for irregular ceiling construction, and for high ceiling areas shall be determined according to Appendix A or B in NFPA 72.  Locate duct detectors no closer than 3 feet from air-supply diffusers or return-air openings.  Locate detectors not closer than 12 inches from any part of a lighting fixture.

  - Duct Smoke Detectors:  Comply with NFPA72 and NFPA90A.  Install sampling tubes so they extend the full width of duct.  Install one Remote Alarm & Test indicator unit directly beneath each duct detector.

  - Install Notification Appliance Devices between 80 and 96 inches on the wall AFF.  Verify that each strobe unit complies with candela requirements for the application.

  - Remote Keypad Annunciators:  Install with top of panel not more than 56 inches above the finished floor.

- IDENTIFICATION

Provide label identification for each device not commonly identified or as requested by the AHJ. This includes 120vac power source with panel label and exact location inside the fire alarm and NAC panels.

- GROUNDING

Verify that all panels are properly grounded for compliance with NEC & local code.

- DEMONSTRATION & TESTING

  - Field tests shall be witnessed by Architect, Engineer and AHJ.  Prior to performing the final test, require a certified service representative to inspect, test, and adjust all components, assemblies, and equipment installations, including all connections to verify the system integrity.

  - Perform Final Tests for the AHJ.  Utilize a certified service representative factory trained on this equipment to perform all testing for the authorities.  Verify each and every device is tested on full AC power and on DC backup power for authorities.  Conduct a complete visual inspection of all devices and controls.

- COMPLETION

  - At the end of the successful test provide completed Record Drawings and system documentation that is required by Sections F, G, H & I above.  Comply with "Inspection Frequencies" Table in the "Inspection" section of NFPA 72 and Testing and Maintenance" Chapters in NFPA 72.  One set of completed "As Built" drawings along with one set of a bound "Maintenance Manual" will be kept on site for AHJ viewing and inspections.  The balance of the required documents referred to in Sections F, G, H & I are to be passed to the Owner & AHJ as required.  Fire-alarm system will be considered defective if it does not pass the final test and inspection.  Prepare the results of the final test and witness documentation to be included in the "As Built" drawings kept on site.

  - Maintenance Test and Inspection:  Perform tests and inspections listed for weekly, monthly, quarterly, and semiannual periods as prescribed in NFPA 72.  Use forms developed for initial tests and inspections. Annual Test and Inspection:  During the one year warranty period and after, each year perform a complete test of the fire-alarm system complying with visual and testing inspection requirements in NFPA 72.  Use forms developed for initial tests and inspections or as currently complying.  Detector Sensitivity Testing: Each year the contractor is to perform detector sensitivity testing and provide a downloaded report to the Owner after cleaning & any re-calibration is performed.  Should any detector fall outside of its sensitivity window, the system will automatically indicate a device trouble for that address.  Engage a factory trained service representative to train the Owner's maintenance personnel to perform minimal adjustments, operation, and basic maintenance of the fire-alarm system between certified authority inspections.

END OF SECTION – FIRE ALARM

NAPCO GEMC Fire Alarm Specification v.01