## Intro
NAPCO Commercial Standby Current Calculation Worksheet
1 Choose the tab that reflects the correct panel configuration for your installation:
1 GEMC-COMBO with GEMC-BM-PS
Use to to calclaute standby current draw of fire section of combo panel
1a GEMC-BM/PS BURG STNDBY ONLY
Use to to calclaute standby current draw of burglary devices powered through GEMC-BM/PS Burg Module
2 GEMC-COMBO with GEMC-BM
3 GEMC Fire Only
4 GEMC Burg Only
5 Auxilliary 12V Power Supply GEMC-12AVPS-CF
6 GEMC Burg SLC Device Load, Wire and Distance Calculator
7 NAC Device Voltage Drop Calculator
2 Enter the quantity for each respective fire device listed that applies to the installation
3 Enter the required Standby and Alarm times for the installation:
|  | ● | BURGLAR ALARM STANDBY TIME
|  | ● | BURGLAR ALARM STANDBY TIME (if applicable)
|  | ● | FIRE ALARM STANDBY TIME
Enter the Battery Derating Factor required by your AHJ (Default = 20%)
|  | ● | BATTERY DERATING FACTOR
Special Notes:
For each NAC Circuit used, enter the total current drawn by the notification appliances connected to each loop used and enter a 1 in the QTY column
For the Control Panel AUX PWR and RELAY PWR terminals (only if wet relay used) enter the total current drawn by the connected devices and enter a 1 in the respective QTY column
For the Control Panel GEMC-F8ZCPIM AUX PWR and GEMC-F8ZCPIM RST PWR terminals (only if wet relay used) enter the total current drawn by the connected devices and enter a 1 in the respective QTY column
Enter the total current drawn by the devices attached to the GEM-BM Burg AUX PWR and RLY PWR terminals. Enter a 1 in the QTY column
Enter the total alarm current drawn by the sounding devices connected to the Burg Bell terminal of the GEM-BM and enter a 1 in the QTY column
Enter the total current drawn by devices connected to the PGM1, PGM2 and Burg Relay terminals of the GEM-BM and enter a 1 in the respective QTY columns

## 1 GEMC-COMBO+GEMC-BM-PS
| GEMC COMBO BURG / FIRE STANDBY CALCULATION CHART (with GEMC-BM/PS) | [6 empty] | Date:
Project Name:
Location:
Prepared By:
Panel Model #:
MODULE | DESCRIPTION | 12V Standby Current (mA) | 12V Alarm Current (mA) | 18V standby loop current | 32V standby loop current | 32V ALARM loop current | 24V Standby Current (mA) | 24V Alarm Current (mA) | QTY | TOTAL STANDBY CURRENT (mA) | TOTAL ALARM CURRENT (mA)
Fire Alarm Current Chart
GEMC-CONTROL PANEL | Control Panel | [5 empty] | 96 | 96 | 1 | 96 | 96
| Fire Aux Relay Normally Energized | [5 empty] | 35 | 35
GEMC-F8ZCPIM | Conventional (8)zone 2-wire fire input module. | 120 |  |  |  |  | 72 | 72
| # of Zones Used | 5 |  |  |  |  | 3 | 24
Devices powered by GEMC-F8ZCPIM AUX PWR
Devices powered by GEMC-F8ZCPIM RST PWR
GEMC-FK1 | LCD Fire Keypad for GEM-C Combo System, Red | 110 |  |  |  |  | 66 | 66
GEMC-RECV | Commercial Fire Wireless Receiver (Fire Bus Only) | 70 |  |  |  |  | 42 | 42
GEMC-EZM8 | 8 Point Expansion Module | 60 |  |  |  |  | 36 | 36
GEMC-FPRINT | Printer Module | 90 |  |  |  |  | 54 | 54
GEMC-RM3008 | Relay Output Module (Fire Bus Only) | 22 |  |  |  |  | 13.2 | 13.2
| # of Relays Normally Energized | 12 |  |  |  |  | 7.2
| # of Relays Energized on Alarm | 12 |  |  |  |  | 0 | 7.2
GEMC-NL-MOD | Internet Reporting Module | 85 |  |  |  |  | 51 | 51
GEMC-RS232 | RS232 Adaptor | 60 |  |  |  |  | 36 | 36
GEMC-OUT8 | PGM Output Module | 35 |  |  |  |  | 21 | 21
GEMC-FW-SLC | Addressable SLC Fire Module | [5 empty] | 70 | 140
FWC-FSLC-SMK | Addressable SLC Photo Smoke Detector |  |  |  | 0.39 | 0.8 | 0.6825 | 1.4
FWC-FSLC-HEAT | Addressable SLC Heat Detector |  |  |  | 0.35 | 0.5 | 0.6125 | 0.875
FWC-FSLC-DUCT | Addressable SLC Photo Duct Smoke Detector |  |  |  | 0.39 | 0.54 | 10.6825 | 0.945
FWC-FSLC-EZM2 | Addressable SLC 2 Zone Conv. Input Module |  |  |  | 0.6 | 0.72 | 1.05 | 1.26
FWC-FSLC-EZM1 | Addressable SLC Single Input Conv.Input Module. |  |  |  | 0.55 | 0.66 | 0.9625 | 1.155
FWC-FSLC-CZM | Addressable SLC Conv Single Module |  |  |  | 0.67 | 0.72 | 2.1725 | 1.26
FWC-FSLC-RM2 | Addressable SLC Dual Relay Module |  |  |  | 0.39 | 0.4 | 0.6825 | 0.7
FWC-FSLC-ISO | Addressable SLC Fire Isolation Module |  |  |  | 0.27 | 0.27 | 0.4725 | 0.4725
FWC-FSLC-SOM1 | Addressable SLC Fire Supervised Output Module |  |  |  | 0.154 | 0.161 | 1.3895 | 0.28175
FWC-FSLC-PULL | Addressable SLC Fire Pull Station |  |  |  | 0.55 | 0.65 | 0.9625 | 1.1375
GEMC-NAC7S | Remote NAC Extender. | 8 |  |  |  |  | 4.8 | 4.8
GEMC-12V2APS-CF | Remote Supervised 12VDC Power Supply | 8 |  |  |  |  | 4.8 | 4.8
GEMC-24VR | Add On 24V Regulator
NAC A | On Board NAC Circuit A | [5 empty] | N/A
NAC B | On Board NAC Circuit B | [5 empty] | N/A
NAC C | On Board NAC Circuit C | [5 empty] | N/A | 0
NAC D (set to 24V) | On Board NAC Circuit D | [5 empty] | N/A | 0
NAC D (set to 12V) | On Board NAC Circuit D | [5 empty] | N/A
Mother Board AUX PWR | Devices powered by Control Panel AUX PWR
Mother Board RLY PWR | (only if configured for wet operation)
Burglar Alarm Current Chart
GEMC-BSLC | Addressable SLC Burg Module | [5 empty] | 55 | 55
GEMC-BSLC-4PT | Burg Device - 4 Point Input Expansion Module |  |  | 3 |  |  | 2.73 | 2.73
GEMC-BSLC-1PT | Burg Device - 1 Point Input Module |  |  | 2 |  |  | 1.82 | 1.82
GEMC-BSLC-DT | Burg Device - Dual Technology Motion Detector |  |  | 19 |  |  | 17.29 | 17.29
GEMC-BSLC-DT-L | Burg Device - Dual Tech. Mot. Det. - Low Power |  |  | 4 |  |  | 3.64 | 3.64
GEMC-BSLC-PIR | Burg Device - PIR Motion Detector |  |  | 19 |  |  | 17.29 | 17.29
GEMC-BSLC-PIR-L | Burg Device - PIR Motion Detector - Low Power |  |  | 4 |  |  | 3.64 | 3.64
GEMC-BSLC-RLY | Burg Device - 1 Point Output Module (active in alarm) |  |  | 3 |  |  | 2.73 | 7.28
GEMC-BSLC-RLY | Burg Device - 1 Point Output Module (Normally on) |  |  | 8 |  |  | 7.28 | 7.28
BURGLAR ALARM STANDBY CURRENT DRAW | [9 empty] | 0 | mA
REQUIRED BURGLAR ALARM STANDBY TIME | [9 empty] | 4 | Hours
REQUIRED BURGLAR STANDBY BATTERY CAPACITY | [9 empty] | 0 | AH
BURGLAR ALARM CURRENT DRAW | [9 empty] | 0 | mA
REQUIRED BURGLAR ALARM STANDBY TIME | [9 empty] | 15 | Min
REQUIRED BURGLAR ALARM BATTERY CAPACITY | [9 empty] | 0 | AH
FIRE STANDBY CURRENT DRAW | [9 empty] | 96 | mA
REQUIRED FIRE STANDBY TIME | [9 empty] | 24 | Hours
REQUIRED FIRE STANDBY BATTERY CAPACITY | [9 empty] | 2.304 | AH
TOTAL FIRE ALARM CURRENT DRAW | [9 empty] | 96 | mA
REQUIRED FIRE ALARM STANDBY TIME | [9 empty] | 5 | Min
REQUIRED FIRE ALARM BATTERY CAPACITY | [9 empty] | 0.008 | AH
BATTERY DERATING FACTOR | [9 empty] | 20 | %
`
TOTAL REQUIRED STANDBY BATTERY CAPACITY | [9 empty] | 2.89 | AH
INSTALLED BATTERY CAPACITY |  | QTY: |  | AH: | [5 empty] | 0 | AH

## 1a GEMC-BM-PS BURG STNDBY ONLY
| GEMC-BM/PS BURG BATTERY STANDBY CALCULATION CHART | [5 empty] | Date:
Project Name:
Location:
Prepared By:
Panel Model #:
MODULE | DESCRIPTION | 12V standby Current | 12V Alarm Current (mA) | 18V standby loop current | 32V standby loop current | 24V Standby Current mA | 24V Alarm Current mA | QTY | TOTAL STANDBY CURRENT (mA) | TOTAL ALARM CURRENT (mA)
Burglar Alarm Current Chart
GEMC-BM/PS | Burg Module with Power Supply |  |  |  |  | 25 | 25
GEMC-BK1 | LCD Burg Keypad | 110 |  |  |  | 66 | 66
GEMC-BK1 with EZM | LCD Burg Keypad with EZM enabled | 120 |  |  |  | 72 | 72
GEMC-EZM8 | 8 Point Expansion Module | 60 |  |  |  | 36 | 36
GEMC-RM3008 | Relay Output Module | 22 |  |  |  | 13.2 | 13.2
| # of Relays Normally Energized | 12 |  |  |  | 7.2 | 7.2
| # of Relays Energized on Alarm |  |  |  |  | 0 | 0
GEMC-OUT8 | PGM Output Module | 35 |  |  |  | 21 | 21
GEMC-12V2APS-R | Remote Supervised 12VDC Power Supply | 8 |  |  |  | 4.8 | 4.8
Burg AUX PWR | (devices powered by AUX PWR)
Burg RLY PWR | (only if configured for wet operation)
Burg Bell | (current draw of Burg sounding appliance)
Burg Relay | (only if configured for wet operation)
BURGLAR ALARM STANDBY CURRENT DRAW | [8 empty] | 0 | mA
REQUIRED BURGLAR ALARM STANDBY TIME | [8 empty] | 4 | Hours
REQUIRED BURGLAR STANDBY BATTERY CAPACITY | [8 empty] | 0 | AH
BURGLAR ALARM CURRENT DRAW | [8 empty] | 0 | mA
REQUIRED BURGLAR ALARM STANDBY TIME | [8 empty] | 15 | Min
REQUIRED BURGLAR ALARM BATTERY CAPACITY | [8 empty] | 0 | AH
BATTERY DERATING FACTOR | [8 empty] | 20 | %
TOTAL REQUIRED STANDBY BATTERY CAPACITY | [8 empty] | 0 | AH
INSTALLED BATTERY CAPACITY |  |  | QTY: |  |  | AH: |  |  | 0 | AH

## 2 GEMC-COMBO+GEMC-BM
| GEMC COMBO BURG / FIRE STANDBY CALCULATION CHART (with GEMC-BM) | [6 empty] | Date:
Project Name:
Location:
Prepared By:
Panel Model #:
MODULE | DESCRIPTION | 12V Standby Current (mA) | 12V Alarm Current (mA) | 18V standby loop current | 32V standby loop current | 32V ALARM loop current | 24V Standby Current (mA) | 24V Alarm Current (mA) | QTY | TOTAL STANDBY CURRENT (mA) | TOTAL ALARM CURRENT (mA)
Fire Alarm Current Chart
GEMC-CONTROL PANEL | Control Panel | [5 empty] | 96 | 96 | 1 | 96 | 96
| Fire Aux Relay Normally Energized | [5 empty] | 35 | 35
GEMC-F8ZCPIM | Conventional (8)zone 2-wire fire input module. | 120 |  |  |  |  | 72 | 72
| # of Zones Used | 5 |  |  |  |  | 3 | 24
Devices powered by GEMC-F8ZCPIM AUX PWR
Devices powered by GEMC-F8ZCPIM RST PWR
GEMC-FK1 | LCD Fire Keypad for GEM-C Combo System, Red | 110 |  |  |  |  | 66 | 66
GEMC-RECV | Commercial Fire Wireless Receiver (Fire Bus Only) | 70 |  |  |  |  | 42 | 42
GEMC-EZM8 | 8 Point Expansion Module | 60 |  |  |  |  | 36 | 36
GEMC-FPRINT | Printer Module | 90 |  |  |  |  | 54 | 54
GEMC-RM3008 | Relay Output Module (Fire Bus Only) | 22 |  |  |  |  | 13.2 | 13.2
| # of Relays Normally Energized | 12 |  |  |  |  | 7.2
| # of Relays Energized on Alarm | 12 |  |  |  |  | 0 | 7.2
GEMC-NL-MOD | Internet Reporting Module | 85 |  |  |  |  | 51 | 51
GEMC-RS232 | RS232 Adaptor | 60 |  |  |  |  | 36 | 36
GEMC-OUT8 | PGM Output Module | 35 |  |  |  |  | 21 | 21
GEMC-FW-SLC | Addressable SLC Fire Module | [5 empty] | 70 | 140
FWC-FSLC-SMK | Addressable SLC Photo Smoke Detector |  |  |  | 0.39 | 0.8 | 0.6825 | 1.4
FWC-FSLC-HEAT | Addressable SLC Heat Detector |  |  |  | 0.35 | 0.5 | 0.6125 | 0.875
FWC-FSLC-DUCT | Addressable SLC Photo Duct Smoke Detector |  |  |  | 0.39 | 0.54 | 10.6825 | 0.945
FWC-FSLC-EZM2 | Addressable SLC 2 Zone Conv. Input Module |  |  |  | 0.6 | 0.72 | 1.05 | 1.26
FWC-FSLC-EZM1 | Addressable SLC Single Input Conv.Input Module. |  |  |  | 0.55 | 0.66 | 0.9625 | 1.155
FWC-FSLC-CZM | Addressable SLC Conv Single Module |  |  |  | 0.67 | 0.72 | 2.1725 | 1.26
FWC-FSLC-RM2 | Addressable SLC Dual Relay Module |  |  |  | 0.39 | 0.4 | 0.6825 | 0.7
FWC-FSLC-ISO | Addressable SLC Fire Isolation Module |  |  |  | 0.27 | 0.27 | 0.4725 | 0.4725
FWC-FSLC-SOM1 | Addressable SLC Fire Supervised Output Module |  |  |  | 0.154 | 0.161 | 1.3895 | 0.28175
FWC-FSLC-PULL | Addressable SLC Fire Pull Station |  |  |  | 0.55 | 0.65 | 0.9625 | 1.1375
GEMC-NAC7S | Remote NAC Extender. | 8 |  |  |  |  | 4.8 | 4.8
GEMC-12V2APS-CF | Remote Supervised 12VDC Power Supply | 8 |  |  |  |  | 4.8 | 4.8
GEMC-24VR | Add On 24V Regulator
NAC A | On Board NAC Circuit A | [5 empty] | N/A
NAC B | On Board NAC Circuit B | [5 empty] | N/A
NAC C | On Board NAC Circuit C | [5 empty] | N/A
NAC D (set to 24V) | On Board NAC Circuit D | [5 empty] | N/A
NAC D (set to 12V) | On Board NAC Circuit D | [5 empty] | N/A
Mother Board AUX PWR
Mother Board RLY PWR | (only if configured for wet operation)
Burglar Alarm Current Chart
GEMC-BM | Burg Module | [5 empty] | 25 | 25
GEMC-BSLC | Addressable SLC Burg Module | [5 empty] | 55 | 55
GEMC-BK1 | LCD Burg Keypad | 110 |  |  |  |  | 66 | 66
GEMC-BK1 with EZM | LCD Burg Keypad with EZM enabled | 120 |  |  |  |  | 72 | 72
GEMC-BSLC-4PT | Burg Device - 4 Point Input Expansion Module |  |  | 3 |  |  | 2.73 | 2.73
GEMC-BSLC-1PT | Burg Device - 1 Point Input Module |  |  | 2 |  |  | 1.82 | 1.82
GEMC-BSLC-DT | Burg Device - Dual Technology Motion Detector |  |  | 19 |  |  | 17.29 | 17.29
GEMC-BSLC-DT-L | Burg Device - Dual Tech. Mot. Det. - Low Power |  |  | 19 |  |  | 4 | 4
GEMC-BSLC-PIR | Burg Device - PIR Motion Detector |  |  | 19 |  |  | 17.29 | 17.29
GEMC-BSLC-PIR-L | Burg Device - PIR Motion Detector - Low Power |  |  | 19 |  |  | 4 | 4
GEMC-BSLC-RLY | Burg Device - 1 Point Output Module (active in alarm) |  |  | 3 |  |  | 2.73 | 7.28
GEMC-BSLC-RLY | Burg Device - 1 Point Output Module (Normally on) |  |  | 8 |  |  | 7.28 | 7.28
GEMC-EZM8 | 8 Point Expansion Module | 60 |  |  |  |  | 36 | 36
GEMC-RM3008 | Relay Output Module | 22 |  |  |  |  | 13.2 | 13.2
| # of Relays Normally Energized | 12 |  |  |  |  | 7.2 | 7.2
| # of Relays Energized on Alarm | 12 |  |  |  |  | 0 | 7.2
GEMC-OUT8 | PGM Output Module | 35 |  |  |  |  | 21 | 21
GEMC-12V2APS-R | Remote Supervised 12VDC Power Supply | 8 |  |  |  |  | 4.8 | 4.8
Burg AUX PWR
Burg RLY PWR | (only if configured for wet operation)
Burg Bell
Burg PGM1
Burg PGM2
Burg Relay | (only if configured for wet operation)
BURGLAR ALARM STANDBY CURRENT DRAW | [9 empty] | 0 | mA
REQUIRED BURGLAR ALARM STANDBY TIME | [9 empty] | 4 | Hours
REQUIRED BURGLAR STANDBY BATTERY CAPACITY | [9 empty] | 0 | AH
BURGLAR ALARM CURRENT DRAW | [9 empty] | 0 | mA
REQUIRED BURGLAR ALARM STANDBY TIME | [9 empty] | 15 | Min
REQUIRED BURGLAR ALARM BATTERY CAPACITY | [9 empty] | 0 | AH
FIRE STANDBY CURRENT DRAW | [9 empty] | 96 | mA
REQUIRED FIRE STANDBY TIME | [9 empty] | 24 | Hours
REQUIRED FIRE STANDBY BATTERY CAPACITY | [9 empty] | 2.304 | AH
TOTAL FIRE ALARM CURRENT DRAW | [9 empty] | 96 | mA
REQUIRED FIRE ALARM STANDBY TIME | [9 empty] | 5 | Min
REQUIRED FIRE ALARM BATTERY CAPACITY | [9 empty] | 0.008 | AH
BATTERY DERATING FACTOR | [9 empty] | 20 | %
TOTAL REQUIRED STANDBY BATTERY CAPACITY | [9 empty] | 2.89 | AH
INSTALLED BATTERY CAPACITY |  | QTY: |  |  |  |  | AH: |  |  | 0 | AH

## 3 GEMC Fire Only
| GEMC FIRE STANDBY CALCULATION CHART | [6 empty] | Date:
Project Name:
Location:
Prepared By:
Panel Model #:
MODULE | DESCRIPTION | 12V standby Current | 12V Alarm Current (mA) | 18V standby loop current | 32V standby loop current | 32V ALARM loop current | 24V Standby Current mA | 24V Alarm Current mA | QTY | TOTAL STANDBY CURRENT (mA) | TOTAL ALARM CURRENT (mA)
Fire Alarm Current Chart
GEMC-CONTROL PANEL | Control Panel | [5 empty] | 96 | 96 | 1 | 96 | 96
| Fire Aux Relay Normally Energized | [5 empty] | 35 | 35
GEMC-F8ZCPIM | Conventional (8)zone 2-wire fire input module. | 120 |  |  |  |  | 72 | 72
| # of Zones Used | 5 |  |  |  |  | 3 | 24
Devices powered by GEMC-F8ZCPIM AUX PWR
Devices powered by GEMC-F8ZCPIM RST PWR
GEMC-FK1 | LCD Fire Keypad for GEM-C Combo System, Red | 110 |  |  |  |  | 66 | 66
GEMC-RECV | Commercial Fire Wireless Receiver (Fire Bus Only) | 70 |  |  |  |  | 42 | 42
GEMC-EZM8 | 8 Point Expansion Module | 60 |  |  |  |  | 36 | 36
GEMC-FPRINT | Printer Module | 90 |  |  |  |  | 54 | 54
GEMC-RM3008 | Relay Output Module (Fire Bus Only) | 22 |  |  |  |  | 13.2 | 13.2
| # of Relays Normally Energized | 12 |  |  |  |  | 7.2
| # of Relays Energized on Alarm | 12 |  |  |  |  | 0 | 7.2
GEMC-NL-MOD | Internet Reporting Module | 85 |  |  |  |  | 51 | 51
GEMC-RS232 | RS232 Adaptor | 60 |  |  |  |  | 36 | 36
GEMC-OUT8 | PGM Output Module | 35 |  |  |  |  | 21 | 21
GEMC-FW-SLC | Addressable SLC Fire Module | [5 empty] | 70 | 140
FWC-FSLC-SMK | Addressable SLC Photo Smoke Detector |  |  |  | 0.39 | 0.8 | 0.6825 | 1.4
FWC-FSLC-HEAT | Addressable SLC Heat Detector |  |  |  | 0.35 | 0.5 | 0.6125 | 0.875
FWC-FSLC-DUCT | Addressable SLC Photo Duct Smoke Detector |  |  |  | 0.39 | 0.54 | 10.6825 | 0.945
FWC-FSLC-EZM2 | Addressable SLC 2 Zone Conv. Input Module |  |  |  | 0.6 | 0.72 | 1.05 | 1.26
FWC-FSLC-EZM1 | Addressable SLC Single Input Conv.Input Module. |  |  |  | 0.55 | 0.66 | 0.9625 | 1.155
FWC-FSLC-CZM | Addressable SLC Conv Single Module |  |  |  | 0.67 | 0.72 | 2.1725 | 1.26
FWC-FSLC-RM2 | Addressable SLC Dual Relay Module |  |  |  | 0.39 | 0.4 | 0.6825 | 0.7
FWC-FSLC-ISO | Addressable SLC Fire Isolation Module |  |  |  | 0.27 | 0.27 | 0.4725 | 0.4725
FWC-FSLC-SOM1 | Addressable SLC Fire Supervised Output Module |  |  |  | 0.154 | 0.161 | 1.3895 | 0.28175
FWC-FSLC-PULL | Addressable SLC Fire Pull Station |  |  |  | 0.55 | 0.65 | 0.9625 | 1.1375
GEMC-NAC7S | Remote NAC Extender. | 8 |  |  |  |  | 4.8 | 4.8
GEMC-12V2APS-CF | Remote Supervised 12VDC Power Supply | 8 |  |  |  |  | 4.8 | 4.8
GEMC-24VR | Add On 24V Regulator
NAC A | On Board NAC Circuit A | [5 empty] | N/A
NAC B | On Board NAC Circuit B | [5 empty] | N/A
NAC C | On Board NAC Circuit C | [5 empty] | N/A
NAC D (set to 24V) | On Board NAC Circuit D | [5 empty] | N/A
NAC D (set to 12V) | On Board NAC Circuit D | [5 empty] | N/A
Mother Board AUX PWR
Mother Board RLY PWR | (only if configured for wet operation)
FIRE STANDBY CURRENT DRAW | [9 empty] | 96 | mA
REQUIRED FIRE STANDBY TIME | [9 empty] | 24 | Hours
REQUIRED FIRE STANDBY BATTERY CAPACITY | [9 empty] | 2.304 | AH
TOTAL FIRE ALARM CURRENT DRAW | [9 empty] | 96 | mA
REQUIRED FIRE ALARM STANDBY TIME | [9 empty] | 5 | Min
REQUIRED FIRE ALARM BATTERY CAPACITY | [9 empty] | 0.008 | AH
BATTERY DERATING FACTOR | [9 empty] | 20 | %
TOTAL REQUIRED STANDBY BATTERY CAPACITY | [9 empty] | 2.89 | AH
INSTALLED BATTERY CAPACITY |  | QTY: |  |  |  |  | AH: |  |  | 0 | AH

## 4 GEMC Burg Only
| GEMC COMBO BURG / FIRE STANDBY CALCULATION CHART (with GEMC-BM) | [5 empty] | Date:
Project Name:
Location:
Prepared By:
Panel Model #:
MODULE | DESCRIPTION | 12V standby Current | 12V Alarm Current (mA) | 18V standby loop current | 32V standby loop current | 24V Standby Current mA | 24V Alarm Current mA | QTY | TOTAL STANDBY CURRENT (mA) | TOTAL ALARM CURRENT (mA)
Burglar Alarm Current Chart
GEMC-CONTROL PANEL | Control Panel |  |  |  |  | 96 | 96 | 1 | 96 | 96
| Fire Aux Relay Normally Energized |  |  |  |  | 35 | 35
GEMC-NL-MOD | Internet Reporting Module | 85 |  |  |  | 51 | 51
GEMC-RS232 | RS232 Adaptor | 60 |  |  |  | 36 | 36
GEMC-BM | Burg Module |  |  |  |  | 25 | 25
GEMC-BSLC | Addressable SLC Burg Module |  |  |  |  | 55 | 55
GEMC-BK1 | LCD Burg Keypad | 110 |  |  |  | 66 | 66
GEMC-BK1 with EZM | LCD Burg Keypad with EZM enabled | 120 |  |  |  | 72 | 72
GEMC-BSLC-4PT | Burg Device - 4 Point Input Expansion Module |  |  | 3 |  | 2.73 | 2.73
GEMC-BSLC-1PT | Burg Device - 1 Point Input Module |  |  | 2 |  | 1.82 | 1.82
GEMC-BSLC-DT | Burg Device - Dual Technology Motion Detector |  |  | 19 |  | 17.29 | 17.29
GEMC-BSLC-DT-L | Burg Device - Dual Tech. Mot. Det. - Low Power |  |  | 19 |  | 4 | 4
GEMC-BSLC-PIR | Burg Device - PIR Motion Detector |  |  | 19 |  | 17.29 | 17.29
GEMC-BSLC-PIR-L | Burg Device - PIR Motion Detector - Low Power |  |  | 19 |  | 4 | 4
GEMC-BSLC-RLY | Burg Device - 1 Point Output Module (active in alarm) |  |  | 3 |  | 2.73 | 7.28
GEMC-BSLC-RLY | Burg Device - 1 Point Output Module (Normally on) |  |  | 8 |  | 7.28 | 7.28
GEMC-EZM8 | 8 Point Expansion Module | 60 |  |  |  | 36 | 36
GEMC-RM3008 | Relay Output Module | 22 |  |  |  | 13.2 | 13.2
| # of Relays Normally Energized | 12 |  |  |  | 7.2 | 7.2
| # of Relays Energized on Alarm | 12 |  |  |  | 0 | 7.2
GEMC-OUT8 | PGM Output Module | 35 |  |  |  | 21 | 21
GEMC-12V2APS-R | Remote Supervised 12VDC Power Supply | 8 |  |  |  | 4.8 | 4.8
Burg AUX PWR | [5 empty] | 0 | 0
Burg RLY PWR | (only if configured for wet operation) |  |  |  |  | 0 | 0
Burg Bell
Burg PGM1
Burg PGM2
Burg Relay | (only if configured for wet operation)
BURGLAR ALARM STANDBY CURRENT DRAW | [8 empty] | 96 | mA
REQUIRED BURGLAR ALARM STANDBY TIME | [8 empty] | 4 | Hours
REQUIRED BURGLAR STANDBY BATTERY CAPACITY | [8 empty] | 0.384 | AH
BURGLAR ALARM CURRENT DRAW | [8 empty] | 96 | mA
REQUIRED BURGLAR ALARM STANDBY TIME | [8 empty] | 15 | Min
REQUIRED BURGLAR ALARM BATTERY CAPACITY | [8 empty] | 0.024 | AH
BATTERY DERATING FACTOR | [8 empty] | 20 | %
TOTAL REQUIRED STANDBY BATTERY CAPACITY | [8 empty] | 0.51 | AH
INSTALLED BATTERY CAPACITY |  | QTY: |  |  |  | AH: |  |  | 0 | AH

## 5 GEMC-12VAPS-CF
| GEMC-12VAPS-CF AUXILLARY POWER SUPPLY STANDBY CALCULATION CHART |  |  |  | Date:
Project Name:
Location:
Prepared By:
Panel Model #:
MODULE | DESCRIPTION | 12V standby Current | 12V Alarm Current (mA) |  |  | QTY | TOTAL STANDBY CURRENT (mA) | TOTAL ALARM CURRENT (mA)
Fire Alarm Current Chart
GEMC-12VAPS MAIN PCB | Control Panel | 40 | 40 |  |  | 1 | 40 | 40
| NO AC(-) Output (if connected) | 0 | 0
| BATT TBL (-) (if connected) | 0 | 0
| TBL (-) (if conncted) | 0 | 0
GEMC-FK1 | LCD Fire Keypad for GEM-C Combo System, Red | 110 | 110
GEMC-RECV | Commercial Fire Wireless Receiver (Fire Bus Only) | 70 | 70
GEMC-EZM8 | 8 Point Expansion Module | 60 | 60
GEMC-FPRINT | Printer Module | 90 | 90
GEMC-RM3008 | Relay Output Module (Fire Bus Only) | 22 | 22
| # of Relays Normally Energized | 12 | 12
| # of Relays Energized on Alarm | 12 | 12
GEMC-NL-MOD | Internet Reporting Module | 85 | 85
GEMC-RS232 | RS232 Adaptor | 60 | 60
GEMC-OUT8 | PGM Output Module | 35 | 35
Additional Devices Not Listed Above
FIRE STANDBY CURRENT DRAW |  |  |  |  | ` |  | 40 | mA
REQUIRED FIRE STANDBY TIME | [6 empty] | 24 | Hours
REQUIRED FIRE STANDBY BATTERY CAPACITY | [6 empty] | 0.96 | AH
TOTAL FIRE ALARM CURRENT DRAW | [6 empty] | 40 | mA
REQUIRED FIRE ALARM STANDBY TIME | [6 empty] | 5 | Min
REQUIRED FIRE ALARM BATTERY CAPACITY | [6 empty] | 0.0033333 | AH
BATTERY DERATING FACTOR | [6 empty] | 20 | %
TOTAL REQUIRED STANDBY BATTERY CAPACITY | [6 empty] | 1.2042 | AH
INSTALLED BATTERY CAPACITY |  | QTY: |  | AH: |  |  | 0 | AH

## 6 BURG SLC CALCS
|  | RUN 1 |  | RUN 2 |  | RUN 3 |  | RUN 4
GEMC BURG SLC DEVICE
DEVICE | CURRENT | QTY |  | QTY |  | QTY |  | QTY |  | TOTAL (ALL)
# GEMC-BSLC-1PT | 0.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | LOAD CALCULATOR
# GEMC-BSLC-4PT | 0.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
# GEMC-BSLC-RLY | 0.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
# GEMC-BSLC-PIR | 0.019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Use this calculator to determine the maximum wire length, gauge to be used and voltage drop depending on your burg devices and wiring method used
# GEMC-BSLC-PIR-L | 0.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
# GEMC-BSLC-DT | 0.019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
# GEMC-BSLC-DT-L | 0.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
# GEMC-BSLC-GB | 0.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total current |  | 0 | + | 0 | + | 0 | + | 0 | = | 0 | AMPS
Number of devices |  | 0 | + | 0 | + | 0 | + | 0 | = | 0 | DEVICES
LOOP WIRE GAUGE | OHMS per foot | Loop Length (feet) |  | Loop Length (feet) |  | Loop Length (feet) |  | Loop Length (feet) |  |  | Single Run |  |  | Multi-Run STAR Configuration (4 parallel runs)
22AWG | 0.0322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20AWG | 0.0203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18AWG | 0.0127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16AWG | 0.0083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14AWG | 0.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | RUN 4
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CASE 1: MORE THAN 80% OF THE DEVICES ARE LOCATED ON THE 2nd HALF OF THE LOOP | [10 empty] | RUN 1
|  | Voltage Drop |  | Voltage Drop |  | Voltage Drop |  | Voltage Drop
BSLC Voltage Drop |  | 0 |  | 0 |  | 0 |  | 0
Wire Voltage Drop |  | 0 |  | 0 |  | 0 |  | 0
Device Interconnections |  | 0 |  | 0 |  | 0 |  | 0
Total Drop (must be < 4) |  | 0 |  | 0 |  | 0 |  | 0 | [7 empty] | RUN 3
CASE 2: THE DEVICES ARE SPREAD OUT EVENLY ACROSS THE ENTIRE LOOP | [12 empty] | RUN 1 |  | RUN 2
|  | Voltage Drop |  | Voltage Drop |  | Voltage Drop |  | Voltage Drop
BSLC Voltage Drop |  | 0 |  | 0 |  | 0 |  | 0
Wire Voltage Drop |  | 0 |  | 0 |  | 0 |  | 0
Device Interconnections |  | 0 |  | 0 |  | 0 |  | 0
Total Drop (must be < 4) |  | 0 |  | 0 |  | 0 |  | 0
CONFIGURABLE PARAMETERS |  | DEFAULTS
BSLC Internal Resistance | 4.5 | 4.5
Device Interconnect Resist | 0.037 | 0.037
22 AWG Resistance/1000 ft | 32.2 | 32.2
20 AWG Resistance/1000 ft | 20.3 | 20.3
18 AWG Resistance/1000 ft | 12.7 | 12.7
16 AWG Resistance/1000 ft | 8.3 | 8.3
14 AWG Resistance/1000 ft | 5 | 5
GEMC Burglay SLC Loop Load Calculator |  | Rev: 3
BSLC
BSLC

## 7 VD CALCS NAC-A
NAPCO GEM-C NAC A DEVICE VOLTAGE CALCULATOR |  | PROJECT: |  |  | DATE:
1-Select your WIRE GAUGE
2-Select your DEVICES types 1>30
3-Determine the wire length distance for each DEVICE from the previous DEVICE in FEET
4-The Voltage at each device will appear far right, if any voltage cell color appears as RED you must use the next higher wire GAUGE
| Select Wire Gauge |  | Wire Pair Ohms Per Foot
| Click here to select Wire Gauge |  | 2 Wire/Ohms/Ft
Dev. Num | Device Type-Part Number | Part Number | Device Alarm Current AMPS | Min Device Voltage | Device Distance (FEET) From Previous Device/ Panel | Voltage at Each Device
1 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
2 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
3 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
4 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
5 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
6 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
7 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
8 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
9 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
10 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
11 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
12 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
13 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
14 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
15 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
16 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
17 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
18 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
19 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
20 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
21 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
22 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
23 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
24 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
25 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
26 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
27 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
28 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
29 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
30 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
| Total Current (Amps) |  | 0

## NAC-B
NAPCO GEM-C NAC B DEVICE VOLTAGE CALCULATOR |  | PROJECT: |  |  | DATE:
1-Select your WIRE GAUGE
2-Select your DEVICES types 1>30
3-Determine the wire length distance for each DEVICE from the previous DEVICE in FEET
4-The Voltage at each device will appear far right, if any voltage cell color appears as RED you must use the next higher wire GAUGE
| Select Wire Gauge |  | Wire Pair Ohms Per Foot
| Click here to select Wire Gauge |  | 2 Wire/Ohms/Ft
Dev. Num | Device Type-Part Number | Part Number | Device Alarm Current AMPS | Min Device Voltage | Device Distance (FEET) From Previous Device/ Panel | Voltage at Each Device
1 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
2 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
3 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
4 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
5 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
6 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
7 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
8 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
9 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
10 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
11 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
12 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
13 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
14 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
15 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
16 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
17 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
18 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
19 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
20 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
21 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
22 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
23 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
24 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
25 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
26 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
27 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
28 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
29 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
30 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
| Total Current (Amps) |  | 0

## NAC-C
NAPCO GEM-C NAC C DEVICE VOLTAGE CALCULATOR |  | PROJECT: |  |  | DATE:
1-Select your WIRE GAUGE
2-Select your DEVICES types 1>30
3-Determine the wire length distance for each DEVICE from the previous DEVICE in FEET
4-The Voltage at each device will appear far right, if any voltage cell color appears as RED you must use the next higher wire GAUGE
| Select Wire Gauge |  | Wire Pair Ohms Per Foot
| Click here to select Wire Gauge |  | 2 Wire/Ohms/Ft
Dev. Num | Device Type-Part Number | Part Number | Device Alarm Current AMPS | Min Device Voltage | Device Distance (FEET) From Previous Device/ Panel | Voltage at Each Device
1 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
2 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
3 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
4 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
5 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
6 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
7 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
8 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
9 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
10 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
11 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
12 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
13 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
14 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
15 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
16 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
17 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
18 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
19 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
20 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
21 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
22 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
23 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
24 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
25 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
26 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
27 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
28 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
29 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
30 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
| Total Current (Amps) |  | 0

## NAC-D
NAPCO GEM-C NAC D DEVICE VOLTAGE CALCULATOR |  | PROJECT: |  |  | DATE:
1-Select your WIRE GAUGE
2-Select your DEVICES types 1>30
3-Determine the wire length distance for each DEVICE from the previous DEVICE in FEET
4-The Voltage at each device will appear far right, if any voltage cell color appears as RED you must use the next higher wire GAUGE
| Select Wire Gauge |  | Wire Pair Ohms Per Foot
| Click here to select Wire Gauge |  | 2 Wire/Ohms/Ft
Dev. Num | Device Type-Part Number | Part Number | Device Alarm Current AMPS | Min Device Voltage | Device Distance (FEET) From Previous Device/ Panel | Voltage at Each Device
1 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
2 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
3 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
4 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
5 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
6 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
7 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
8 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
9 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
10 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
11 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
12 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
13 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
14 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
15 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
16 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
17 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
18 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
19 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
20 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
21 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
22 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
23 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
24 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
25 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
26 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
27 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
28 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
29 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
30 | None - Click here to select device from dropdown | None | 0 | 0 | 0 | 0
| Total Current (Amps) |  | 0

## NAC BU
Device Type (MODEL) | Part Number | Alarm Current "Amps" | Minimum Voltage "Volts"
None - Click here to select device from dropdown | None | 0 | 0 | Click here to select Wire Gauge | 2 Wire/Ohms/Ft
Custom 1 |  | 0 | 0 | 12 Gauge | 0.0032
Custom 2 |  | 0 | 0 | 14 Gauge | 0.0055
Custom 3 |  | 0 | 0 | 16 Gauge | 0.008
Custom 4 |  | 0 | 0 | 18 Gauge | 0.0128
Custom 5 |  | 0 | 0 | 22 Gauge | 0.0323
SS-Wall Mount Horn/Strobe-2 Wire Horn Std Candela Red-P2R | P2R | 0.08 | 16
SS-Wall Mount Horn/Strobe-2 Wire Horn Hi Candela Red-P2RH | P2RH | 0.08 | 16
SS-Wall Mount Horn/Strobe-2 Wire Horn Std Candela White-P2W | P2W | 0.08 | 16
SS-Wall Mount Horn/Strobe-2 Wire Horn Hi Candela White-P2WH | P2WH | 0.08 | 16
SS-Wall Mount Horn/Strobe-2 Wire Horn Std Candela Red Outdoor-P2RK | P2RK | 0.08 | 16
SS-Wall Mount Horn/Strobe-2 Wire Horn Hi Candela Red Outdoor-P2RHK | P2RHK | 0.08 | 16
SS-Wall Mount Horn/Strobe-2 Wire Horn Std Candela White Outdoor-P2WK | P2WK | 0.08 | 16
SS-Wall Mount Horn/Strobe-2 Wire Horn Hi Candela White OutdoorP2WHK | P2WHK | 0.08 | 16
SS-Wall Mount Horn/Strobe-4 Wire Horn Std Candela Red-P4R | P4R | 0.08 | 16
SS-Wall Mount Horn/Strobe-4 Wire Horn Hi Candela Red-P4RH | P4RH | 0.08 | 16
SS-Wall Mount Horn/Strobe-4 Wire Horn Std Candela White-P4W | P4W | 0.08 | 16
SS-Wall Mount Horn/Strobe-4 Wire Horn Hi Candela White-P4WH | P4WH | 0.08 | 16
SS-Wall Mount Horn/Strobe-4 Wire Horn Std Candela Red Outdoor-P4RK | P4RK | 0.08 | 16
SS-Wall Mount Horn/Strobe-4 Wire Horn Hi Candela Red Outdoor-P4RHK | P4RHK | 0.08 | 16
SS-Wall Mount Horn/Strobe-4 Wire Horn Std Candela White Outdoor-P4WK | P4WK | 0.08 | 16
SS-Wall Mount Horn/Strobe-4 Wire Horn Hi Candela White Outdoor-P4WHK | P4WHK | 0.08 | 16
SS-Strobe Std Candela Red-SR | SR | 0.36 | 16
SS-Strobe Hi Candela Red-SRH | SRH | 0.36 | 16
SS-Strobe Std Candela White-SW | SW | 0.36 | 16
SS-Strobe Hi Candela White-SWH | SWH | 0.36 | 16
SS-Strobe Std Candela Red Outdoor-SRK | SRK | 0.36 | 16
SS-Strobe Hi Candela Red Outdoor-SRHK | SRHK | 0.36 | 16
SS-Strobe Std Candela White Outdoor-SWK | SWK | 0.36 | 16
SS-Strobe Hi Candela White Outdoor-SWHK | SWHK | 0.36 | 16
SS-Strobe Std Candela White Amber Lens with ALERT-SW-ALERT | SW-ALERT | 0.36 | 16
SS-Strobe Hi Candela White Amber Lens with ALERT-SWH-ALERT | SWH-ALERT | 0.36 | 16
SS-Strobe Std Candela White Clear Lens with ALERT-SW-CLR-ALERT | SW-CLR-ALERT | 0.36 | 16
SS-Wall, Red, Selectable Candela Speaker/Strobe-SPSR | SPSR | 0.22 | 16
SS-Wall, Red, Selectable Candela Speaker/Strobe Plain-SPSR-P | SPSR-P | 0.22 | 16
SS-Wall, Red, Selectable Candela Speaker/Strobe Hi Cad-SPSR-H | SPSR-H | 0.22 | 16
SS-Wall, Red, Selectable Candela Speaker/Strobe Hi Cad Plain-SPSRH-P | SPSRH-P | 0.22 | 16
SS-Wall, White, Selectable Candela Speaker/Strobe-SPSW | SPSW | 0.22 | 16
SS-Wall, White, Selectable Candela Speaker/Strobe, Clear Lens Alert-SPSW-CLR-ALERT | SPSW-CLR-ALERT | 0.22 | 16
SS-Wall, White, Selectable Candela Speaker/Strobe, Amber Lens Alert-SPSW-ALERT | SPSW-ALERT | 0.22 | 16
SS-Wall, White, Selectable Candela Speaker/Strobe Plain-SPSW-P | SPSW-P | 0.22 | 16
SS-Wall, White, Selectable Candela Speaker/Strobe Hi Cad-SPSWH | SPSWH | 0.22 | 16
SS-Wall, White, Selectable Candela Speaker/Strobe Hi Cad Plain-SPSWH-P | SPSWH-P | 0.22 | 16
SS-Wall, White, Selectable Candela Speaker/Strobe Hi db-SPSRV | SPSRV | 0.22 | 16
SS-Wall, White, Selectable Candela Speaker/Strobe Hi db Plain-SPSRV-P | SPSRV-P | 0.22 | 16
SS-Wall, Outdoor Red, Selectable Candela Speaker/Strobe-SPSRK | SPSRK | 0.22 | 16
SS-Wall, Outdoor Red, Selectable Candela Speaker/Strobe-SPSRK-P | SPSRK-P | 0.22 | 16
SS-Wall, Outdoor Red, Selectable Candela Speaker/Strobe replacement-SPSRK-P | SPSRK-R | 0.22 | 16
SS-Wall, Outdoor Red, Selectable Candela Speaker/Strobe Hi Cad-SPSRHK | SPSRHK | 0.22 | 16
SS-Wall, Outdoor White, Selectable Candela Speaker/Strobe-SPSWK | SPSWK | 0.22 | 16
SS-Wall, Outdoor White, Selectable Candela Speaker/Strobe Plain-SPSWK-P | SPSWK-P | 0.22 | 16
SS-Wall, Outdoor White, Selectable Candela Speaker/Strobe Replacement-SPSWK-R | SPSWK-R | 0.22 | 16
SS-Ceiling, Red, Selectable Candela, Speaker/Strobe; Hi Cd-SPSCRH | SPSCRH | 0.22 | 16
SS-Ceiling, White, Selectable Candela, Speaker/Strobe-SPSCW | SPSCW | 0.22 | 16
SS-Ceiling, White, Selectable Candela, Speaker/Strobe, clear lens alert-SPSCW-CLR-ALERT | SPSCW-CLR-ALERT | 0.22 | 16
SS-Ceiling, White, Selectable Candela, Speaker/Strobe, plain-SPSCW-P | SPSCW-P | 0.22 | 16
SS-Ceiling, White, Selectable Candela, Speaker/Strobe; Hi Cd-SPSCW-H | SPSCWH | 0.22 | 16
SS-Ceiling, White, Selectable Candela, Speaker/Strobe; Hi Cd, plain-SPSCWH-P | SPSCWH-P | 0.22 | 16
SS-Ceiling, Red, Selectable Candela, Speaker/Strobe, Hi dB-SPSCRV | SPSCRV | 0.22 | 16
SS-Ceiling, Red, Selectable Candela, hi dB, Speaker/Strobe; Hi Cd-SPSCRVH | SPSCRVH | 0.22 | 16
SS-Ceiling, White, Selectable Candela, Speaker/Strobe, Hi dB-SPSCWY | SPSCWV | 0.22 | 16
SS-Ceiling, White, Selectable Candela, Speaker/Strobe, Hi dB, plain-SPSCWY-P | SPSCWV-P | 0.22 | 16
SS-Ceiling, White, Selectable Candela, Speaker/Strobe, Hi dB, Hi Cd-SPSCWVH | SPSCWVH | 0.22 | 16
SS-Ceiling, White, Selectable Candela, Speaker/Strobe, Hi db, Hi Cd, Plain-SPSCWVH-P | SPSCWVH-P | 0.22 | 16
SS-Ceiling, Outdoor, White, Selectable Candela, Speaker/Strobe-SPSCWK | SPSCWK | 0.22 | 16
SS-Ceiling, Outdoor, White, Selectable Candela, Speaker/Strobe; Hi Cd-SPSCWHK | SPSCWHK | 0.22 | 16
SS- 2 Wire Horn/Strobe Ceiling Std Candela Red-PC2R | PC2R | 0.27 | 16
SS-2 Wire Horn/Strobe Ceiling Hi Candela Red-PC2RH | PC2RH | 0.27 | 16
SS-2 Wire Horn/Strobe Ceiling Std Candela White-PC2W | PC2W | 0.27 | 16
SS- 2 Wire Horn/Strobe Ceiling Hi Candela White-PC2WH | PC2WH | 0.27 | 16
SS-2 Wire Horn/Strobe Ceiling Std Candela Red Outdoor-PC2RK | PC2RK | 0.27 | 16
SS-2 Wire Horn/Strobe Ceiling Hi Candela Red Outdoor-PC2RHK | PC2RHK | 0.27 | 16
SS- 2 Wire Horn/Strobe Ceiling Std Candela White Outdoor-PC2WK | PC2WK | 0.27 | 16
SS-2 Wire Horn/Strobe Ceiling Hi Candela White Outdoor-PC2WHK | PC2WHK | 0.27 | 16
SS-4 Wire Horn/Strobe Ceiling Std Candela Red-PC4R | PC4R | 0.27 | 16
SS-4 Wire Horn/Strobe Ceiling Hi Candela Red-PC4RH | PC4RH | 0.27 | 16
SS-4 Wire Horn/Strobe Ceiling Std Candela White-PC4W | PC4W | 0.27 | 16
SS-4 Wire Horn/Strobe Ceiling Hi Candela White-PC4WH | PC4WH | 0.27 | 16
SS-4 Wire Horn/Strobe Ceiling Std Candela Red Outdoor-PC4RK | PC4RK | 0.27 | 16
SS-4 Wire Horn/Strobe Ceiling Hi Candela Red Outdoor-PC4RHK | PC4RHK | 0.27 | 16
SS-4 Wire Horn/Strobe Ceiling Std Candela White Outdoor-PC4WK | PC4WK | 0.27 | 16
SS-4 Wire Horn/Strobe Ceiling Hi Candela White Outdoor-PC4WHK | PC4WHK | 0.27 | 16
SS-Strobe Ceiling Std Candela Red-SCR | SCR | 0.36 | 16
SS-Strobe Ceiling Hi Candela Red-SCRH | SCRH | 0.36 | 16
SS-Strobe Ceiling Std Candela White-SCW | SCW | 0.36 | 16
SS- Strobe Ceiling Std Candela White-SCWH | SCWH | 0.36 | 16
SS-Strobe Ceiling Std Candela Red Outdoor-SCRK | SCRK | 0.36 | 16
SS-Strobe Ceiling Hi Candela Red Outdoor-SCRHK | SCRHK | 0.36 | 16
SS-Strobe Ceiling Std Candela White Outdoor-SCWK | SCWK | 0.36 | 16
SS-Strobe Ceiling Hi Candela White Outdoor-SCWHK | SCWHK | 0.36 | 16
SS- 2 Wire Horn/Strobe Wall Std Candela Red - PLAIN-P2RP | P2R-P | 0.27 | 16
SS- 3 Wire Horn/Strobe Wall Std Candela Red - PLAIN Outdoor-P2RKP | P2RK-P | 0.27 | 16
SS- 2 Wire Horn/Strobe Wall Std Candela White- PLAIN-P2W-P | P2W-P | 0.27 | 16
SS- 3 Wire Horn/Strobe Wall Std Candela White- PLAIN Outdoor-P2WK-P | P2WK-P | 0.27 | 16
SS- 2 Wire Horn/Strobe Wall Hi Candela Red - PLAIN-P2RH-P | P2RH-P | 0.27 | 16
SS- 3 Wire Horn/Strobe Wall Hi Candela Red - PLAIN Outdoor-P2RHK-P | P2RHK-P | 0.27 | 16
SS- 2 Wire Horn/Strobe Wall Hi Candela White - PLAIN-P2WH-P | P2WH-P | 0.27 | 16
SS- 3 Wire Horn/Strobe Wall Hi Candela White - PLAIN Outdoor-P2WHK-P | P2WHK-P | 0.27 | 16
SS- 4 Wire Horn/Strobe Wall Std Candela Red - PLAIN-P4R-P4 | P4R-P4 | 0.27 | 16
SS- 4 Wire Horn/Strobe Wall Hi Candela Red - PLAIN-P4RH-P | P4RH-P | 0.27 | 16
SS- 4 Wire Horn/Strobe Wall Std Candela White - PLAIN-P4W-P | P4W-P | 0.27 | 16
SS- 4 Wire Horn/Strobe Wall Hi Candela White - PLAIN-P4WH-P | P4WH-P | 0.27 | 16
SS- Strobe Wall Std Candela Red - PLAIN-SR-P | SR-P | 0.36 | 16
SS- Strobe Wall Std Candela Red - PLAIN Outdoor-SRK-P | SRK-P | 0.36 | 16
SS- Strobe Wall Std Candela White - PLAIN-SW-P | SW-P | 0.36 | 16
SS-Strobe Wall Std Candela White - PLAIN Outdoor-SWK-P | SWK-P | 0.36 | 16
SS-Strobe Wall Hi Candela White -PLAIN-SRH-P | SRH-P | 0.36 | 16
SS- Strobe Wall Hi Candela White -PLAIN Outdoor-SRHK-P | SRHK-P | 0.36 | 16
SS- Strobe Wall Hi Candela White -PLAIN-SWH-P | SWH-P | 0.36 | 16
SS- Strobe Wall Hi Candela White -PLAIN Outdoor-SWHK-P | SWHK-P | 0.36 | 16
SS- 2 Wire Horn/Strobe Ceiling Std Candela Red - PLAIN-PC2R-P | PC2R-P | 0.27 | 16
SS- 2 Wire Horn/Strobe Ceiling Std Candela White - PLAIN-PC2W-P | PC2W-P | 0.27 | 16
SS- 2 Wire Horn/Strobe Ceiling Hi Candela Red - PLAIN-PC2RH-P | PC2RH-P | 0.27 | 16
SS- 2 Wire Horn/Strobe Ceiling Hi Candela White - PLAIN-PC2WH-P | PC2WH-P | 0.27 | 16
SS- Strobe Ceiling Std Candela Red - PLAIN-SCR-P | SCR-P | 0.36 | 16
SS-Strobe Ceiling Std Candela White - PLAIN-SCW-P | SCW-P | 0.36 | 16
SS- Strobe Ceiling Hi Candela Red - PLAIN-SCRH-P | SCRH-P | 0.36 | 16
SS- Strobe Ceiling Hi Candela White - PLAIN-SCWH-P | SCWH-P | 0.36 | 16
SS-Chime, Red-CHR | CHR | 0.28 | 16
SS-Chime, White-CHW | CHW | 0.28 | 16
SS- Chime/Strobe, Red-CHSR | CHSR | 0.28 | 16
SS- Chime/Strobe, White-CHSW | CHSW | 0.28 | 16
HR Horn, Red-HR | HR | 0.08 | 16
HW Horn, White-HW | HW | 0.08 | 16
HRK Horn, Red, Outdoor-HRK | HRK | 0.08 | 16
MHR Mini-Horn, Red-MHR | MHR | 0.08 | 16
MHW Mini-Horn, White-MHW | MHW | 0.08 | 16
SS- Repl 2 Wire Horn/Strobe Wall Hi Candela Red Outdoor-P2RHK-R | P2RHK-R | 0.27 | 16
SS- Repl 2 Wire Horn/Strobe Wall Std Candela Red Outdoorr-P2RK-R | P2RK-R | 0.27 | 16
SS- Repl 2 Wire Horn/Strobe Wall Hi Candela White Outdoorr-P2WHK-R | P2WHK-R | 0.27 | 16
SS- Repl 2 Wire Horn/Strobe Wall Std Candela White Outdoorr-P2WK-R | P2WK-R | 0.27 | 16
SS- Repl 4 Wire Horn/Strobe Wall Hi Candela Red Outdoorr-P4RHK-R | P4RHK-R | 0.27 | 16
SS- Repl 4 Wire Horn/Strobe Wall Std Candela Red Outdoorr-P4RK-R | P4RK-R | 0.27 | 16
SS- Repl Strobe Wall Hi Candela Red Outdoor-SRHK-R | SRHK-R | 0.36 | 16
SS- Repl Strobe Wall Std Candela Red Outdoor-SRK-R | SRK-R | 0.36 | 16
SS- Repl Strobe Wall Hi Candela White Outdoor-SWHK-R | SWHK-R | 0.36 | 16
SS- Repl Strobe Wall Std Candela White Outdoor-SWK-R | SWK-R | 0.36 | 16
SS- Repl Horn Red Outdoor-HRK-R | HRK-R | 0.08 | 16
Compatable Wheelock Syncronizing Horns-AH-12 | AH-12 | 0.08 | 16
Compatable Wheelock Syncronizing Horns-AH-12WP | AH-12WP | 0.08 | 16
Compatable Wheelock Syncronizing Horns-HS-24 | HS-24 | 0.08 | 16
Compatable Wheelock Syncronizing Horns-NH-12/24 | NH-12/24 | 0.08 | 16
Compatable Wheelock Syncronizing Horns-ZNH | ZNH | 0.08 | 16
Compatable Wheelock Syncronizing Horns-AH-24 | AH-24 | 0.08 | 16
Compatable Wheelock Syncronizing Horns-AH-24WP | AH-24WP | 0.08 | 16
Compatable Wheelock Syncronizing Horns-MIZ-24S | MIZ-24S | 0.08 | 16
Compatable Wheelock Syncronizing Horns-HN | HN | 0.08 | 16
Compatable Wheelock Syncronizing Horns-HNC | HNC | 0.08 | 16
Compatable Wheelock Syncronizing Horns Strobes-AS-121575W | AS-121575W | 0.27 | 16
Compatable Wheelock Syncronizing Horns Strobes-AS-241575W | AS-241575W | 0.27 | 16
Compatable Wheelock Syncronizing Horns Strobes-AS-24MCW | AS-24MCW | 0.27 | 16
Compatable Wheelock Syncronizing Horns Strobes-AS-24MCC | AS-24MCC | 0.27 | 16
Compatable Wheelock Syncronizing Horns Strobes-AS-24MCWH | AS-24MCWH | 0.27 | 16
Compatable Wheelock Syncronizing Horns Strobes-AS-24MCCH | AS-24MCCH | 0.27 | 16
Compatable Wheelock Syncronizing Horns Strobes-AS-2415C | AS-2415C | 0.27 | 16
Compatable Wheelock Syncronizing Horns Strobes-AS-2430C | AS-2430C | 0.27 | 16
Compatable Wheelock Syncronizing Horns Strobes-AS-2475W | AS-2475C | 0.27 | 16
Compatable Wheelock Syncronizing Horns Strobes-AS-24100C | AS-24100C | 0.27 | 16
Compatable Wheelock Syncronizing Horns Strobes-ASWP-2475W | ASWP-2475W | 0.27 | 16
Compatable Wheelock Syncronizing Horns Strobes-NS4-121575W | NS4-121575W | 0.27 | 16
Compatable Wheelock Syncronizing Horns Strobes-NS-121575W | NS-121575W | 0.27 | 16
Compatable Wheelock Syncronizing Horns Strobes-HS4-241575W | HS4-241575W | 0.27 | 16
Compatable Wheelock Syncronizing Horns Strobes-NS-2-41575W | NS-2-41575W | 0.27 | 16
Compatable Wheelock Syncronizing Horns Strobes-HS4-24MCW | HS4-24MCW | 0.27 | 16
Compatable Wheelock Syncronizing Horns Strobes-NS-24MCW | NS-24MCW | 0.27 | 16
Compatable Wheelock Syncronizing Horns Strobes-HS4-24MCWH | HS4-24MCWH | 0.27 | 16
Compatable Wheelock Syncronizing Horns Strobes-HS4-24150C | HS4-24150C | 0.27 | 16
Compatable Wheelock Syncronizing Horns Strobes-HS | HS | 0.27 | 16
Compatable Wheelock Syncronizing Horns Strobes-HSC | HSC | 0.27 | 16
Compatable Wheelock Syncronizing Horns Strobes-HS4-24185W | HS4-24185W | 0.27 | 16
Compatable Wheelock Syncronizing Horns Strobes-ZNS-MCW | ZNS-MCW | 0.27 | 16
Compatable Wheelock Syncronizing Horns Strobes-ZNS-MCWH | ZNS-MCWH | 0.27 | 16
Compatable Wheelock Syncronizing Strobes-ZNS-MCWH | ZNS-MCWH | 0.36 | 16
Compatable Wheelock Syncronizing Strobes-RSS-121575W | RSS-121575W | 0.36 | 16
Compatable Wheelock Syncronizing Strobes-RSSP-121575W | RSSP-121575W | 0.36 | 16
Compatable Wheelock Syncronizing Strobes-RSS-241575W | RSS-241575W | 0.36 | 16
Compatable Wheelock Syncronizing Strobes-RSSP-241575W | RSSP-241575W | 0.36 | 16
Compatable Wheelock Syncronizing Strobes-RSS-24MCW | RSS-24MCW | 0.36 | 16
Compatable Wheelock Syncronizing Strobes-RSSP-24MCW | RSSP-24MCW | 0.36 | 16
Compatable Wheelock Syncronizing Strobes-RSS-24MCC | RSS-24MCC | 0.36 | 16
Compatable Wheelock Syncronizing Strobes-RSS-2415CST | RSS-2415C ST | 0.36 | 16
Compatable Wheelock Syncronizing Strobes-RSS-2430C STC | RSS-2430C STC | 0.36 | 16
Compatable Wheelock Syncronizing Strobes-RSS-2475C | RSS-2475C | 0.36 | 16
Compatable Wheelock Syncronizing Strobes-RSS-24100C | RSS-24100C | 0.36 | 16
Compatable Wheelock Syncronizing Strobes-RSS-2415CR | RSS-2415CR | 0.36 | 16
Compatable Wheelock Syncronizing Strobes-RSS-2430CR | RSS-2430CR | 0.36 | 16
Compatable Wheelock Syncronizing Strobes-RSS-2475CR | RSS-2475CR | 0.36 | 16
Compatable Wheelock Syncronizing Strobes-RSS-24100CR | RSS-24100CR | 0.36 | 16
Compatable Wheelock Syncronizing Strobes-RSS-24150C | RSS-24150C | 0.36 | 16
Compatable Wheelock Syncronizing Strobes-RSS-24177C | RSS-24177C | 0.36 | 16
Compatable Wheelock Syncronizing Strobes-RSS-24150W | RSS-24150W | 0.36 | 16
Compatable Wheelock Syncronizing Strobes-RSSP-24150W | RSSP-24150W | 0.36 | 16
Compatable Wheelock Syncronizing Strobes-RSS-24177W | RSS-24177W | 0.36 | 16
Compatable Wheelock Syncronizing Strobes-RSSP-24177W | RSSP-24177W | 0.36 | 16
Compatable Wheelock Syncronizing Strobes-RSS-24185W | RSS-24185W | 0.36 | 16
Compatable Wheelock Syncronizing Strobes-RSSP-24185W | RSSP-24185W | 0.36 | 16
Compatable Wheelock Syncronizing Strobes-RSS-24150CR | RSS-24150CR | 0.36 | 16
Compatable Wheelock Syncronizing Strobes-RSS-24177CR | RSS-24177CR | 0.36 | 16
Compatable Wheelock Syncronizing Strobes-RSSWP-2475W | RSSWP-2475W | 0.36 | 16
Compatable Wheelock Syncronizing Strobes-ZRSMCW | ZRS-MCW | 0.36 | 16
Compatable Wheelock Syncronizing Strobes-ZRSMCWH | ZRS-MCWH | 0.36 | 16
Compatable Wheelock Non-Syncronizing Appliances-MB-G6-12 | MB-G6-12 | 0.36 | 16
Compatable Wheelock Non-Syncronizing Appliances-MB-G6-24 | MB-G6-24 | 0.36 | 16
Compatable Wheelock Non-Syncronizing Appliances-MB-G10-12 | MB-G10-12 | 0.36 | 16
Compatable Wheelock Non-Syncronizing Appliances-MB-G10-24 | MB-G10-24 | 0.36 | 16
Compatable Wheelock Non-Syncronizing Appliances-MIZ-TC12 | MIZ-TC12 | 0.36 | 16
Compatable Wheelock Non-Syncronizing Appliances-MIZ-TC24 | MIZ-TC24 | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-AMT-241575W | AMT-241575W | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-AMT4-241575W | AMT4-241575W | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-AMT-2475W | AMT-2475W | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-AMT4-2475W | AMT4-2475W | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-AMT-241575W-NYC | AMT-241575W-NYC | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-AMT4-241575W-NYC | AMT4-241575W-NYC | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-AMT-2475W-NYC | AMT-2475W-NYC | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-AMT4-2475W-NYC | AMT4-2475W-NYC | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-MT-12575W | MT-12575W | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-MT-241575W | MT-241575W | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-MT-2475W | MT-2475W | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-MTWP-12575W | MTWP-2475W | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-ET70WP-2475W | ET70WP-2475W | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-CH70-24MCW | CH70-24MCW | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-CH30-24MCW | CH90-24MCW | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-CH70-24MCC | CH70-24MCC | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-CH30-24MCW | CH90-24MCC | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-CH70-2415C | CH70-2415C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-CH30-2415C | CH90-2415C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-CH70-2430C | CH70-2430C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-CH30-2430C | CH90-2430C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-CH70-2475C | CH70-2475C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-CH30-2475C | CH90-2475C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-CH70-24100C | CH70-24100C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-CH30-24100C | CH90-24100C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-CH70-24150C | CH70-24150C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-CH30-24150C | CH90-24150C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-CH70-24177C | CH70-24177C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-CH90-24177C | CH90-24177C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-CH70-24150W | CH70-24150W | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-CH90-24150W | CH90-24150W | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-CH70-24MCWH | CH70-24MCWH | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-CH90-24MCWH | CH90-24MCCH | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-CH70-24185W | CH70-24185W | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-CH30-24185W | CH90-24185W | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-E70-24MCW | E70-24MCW | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-E30-24MCW | E90-24MCW | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-E70-24MCC | E70-24MCC | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-E90-24MCC | E90-24MCC | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-E70-2415C | E70-2415C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-E90-2415C | E90-2415C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-E70-2430C | E70-2430C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-E90-2430C | E90-2430C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-E70-2475C | E70-2475C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-E30-2475C | E90-2475C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-E70-24100C | E70-24100C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-E30-24100C | E90-24100C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-E70-24150C | E70-24150C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-E90-24150C | E90-24150C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-E70-24177C | E70-24177C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-E90-24177C | E90-24177C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-E70-24150W | E70-24150W | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-E90-24150W | E90-24150W | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-E70-24MCWH | E70-24MCWH | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-E90-24MCCH | E90-24MCCH | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-E70-24185W | E70-24185W | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-E90-24185W | E90-24185W | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-ET70-24MCW | ET70-24MCW | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-ET30-24MCW | ET90-24MCW | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-ET70-24MCC | ET70-24MCC | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-ET90-24MCC | ET90-24MCC | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-ET70-2415C | ET70-2415C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-ET30-2415C | ET90-2415C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-ET70-2430C | ET70-2430C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-ET90-2430C | ET90-2430C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-ET70-2475C | ET70-2475C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-ET90-2475C | ET90-2475C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-ET70-24100C | ET70-24100C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-ET90-24100C | ET90-24100C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-ET70-24150C | ET70-24150C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-ET90-24150C | ET90-24150C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-ET70-24177C | ET70-24177C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-ET90-24177C | ET90-24177C | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-ET70-24150W | ET70-24150W | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-ET90-24150W | ET90-24150W | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-ET70-24MCWH | ET70-24MCWH | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-ET90-24MCWH | ET90-24MCCH | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-ET70-24185W | ET70-24185W | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-ET90-24185W | EET90-24185W | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-SA-70-24-SL | SA-70-24-SL | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-SA-30-24-SL | SA-90-24-SL | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-SA-70-24-SLM | SA-70-24-SLM | 0.36 | 16
Compatable Wheelock Appliances with Syncronizing Strobes-SA-30-24-SLM | SA-90-24-SLM | 0.36 | 16
Compatable Wheelock Coded Audible Appliances-AMT-12/24 | AMT-12/24 | 0.1 | 16
Compatable Wheelock Coded Audible Appliances-AMT4-12/24 | AMT4-12/24 | 0.1 | 16
Compatable Wheelock Coded Audible Appliances-AMT-12/24-NYC | AMT-12/24-NYC | 0.1 | 16
Compatable Wheelock Coded Audible Appliances-AMT4-12/24-NYC | AMT4-12/24-NYC | 0.1 | 16
Compatable Wheelock Coded Audible Appliances-CH70 | CH70 | 0.1 | 16
Compatable Wheelock Coded Audible Appliances-CH30 | CH90 | 0.1 | 16
Compatable Wheelock Coded Audible Appliances-CSX10-24-DC | CSX10-24-DC | 0.1 | 16
Compatable Wheelock Coded Audible Appliances-CSXG10-24-DC | CSXG10-24-DC | 0.1 | 16
Compatable Wheelock Coded Audible Appliances-MT-12/24 | MT-12/24 | 0.1 | 16
Compatable Wheelock Coded Audible Appliances-MT4-12/24 | MT4-12/24 | 0.1 | 16